## Instructions
SunSpec PICS Template
This SunSpec PICS template was generated by SunSpec Dashboard v1.0.4a based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Certification Info
Certificate Number
Date | 2016-09-29 17:50:13
Manufacturer Name | ABB
Product Name | TRIO solar inverter
Product Models | TRIO-50.0-TL-OUTD, TRIO-50.0-TL-OUTD-US-480
Product Description | Three Phase String Inverter consisting of three separable units: Power Module, DC Wiring Box; AC Wiring Box

## Testing Info
Submitter | Andrea Botarelli
Email | andrea.botarelli@it.abb.com
Phone
Interface Type | RTU
Baud Rate | 19200
Slave Id | 1

## 1
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40002 | ID |  |  | 1
40003 | L |  |  | 66
40004 | Manufacturer (Mn) |  |  | ABB | R
40020 | Model (Md) |  |  | TRIO-50.0-TL-OUTD | R
40036 | Options (Opt) |  |  | -3N62- | R
40044 | Version (Vr) |  |  | 1631F | R | Provided SW release version string is formatted as [Y + WY + DW] where Y is the release year (format YY), WY is the release week of the year (format WW) and DW is the release day of the week (encoded as a single ASCII character starting from 'A' which is associated to Monday)
40052 | Serial Number (SN) |  |  | 0001251016 | R | Provided serial number string is formatted as [SN + WY] where SN is the internal serial number of the unit and WY is the manufacturing week/year date expressed in WWYY format.
40068 | Device Address (DA) |  |  | unimplemented | RW
40069 | Pad |  |  |  | R

## 103
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40070 | ID |  |  | 103
40071 | L |  |  | 50
40072 | Amps (A) |  |  | supported | R
40073 | Amps PhaseA (AphA) |  |  | supported | R
40074 | Amps PhaseB (AphB) |  |  | supported | R
40075 | Amps PhaseC (AphC) |  |  | supported | R
40076 | A_SF |  |  | -1 | R
40077 | Phase Voltage AB (PPVphAB) |  |  | supported | R
40078 | Phase Voltage BC (PPVphBC) |  |  | supported | R
40079 | Phase Voltage CA (PPVphCA) |  |  | supported | R
40080 | Phase Voltage AN (PhVphA) |  |  | supported | R
40081 | Phase Voltage BN (PhVphB) |  |  | supported | R
40082 | Phase Voltage CN (PhVphC) |  |  | supported | R
40083 | V_SF |  |  | -1 | R
40084 | Watts (W) |  |  | supported | R
40085 | W_SF |  |  | 1 | R
40086 | Hz |  |  | supported | R
40087 | Hz_SF |  |  | -2 | R
40088 | VA |  |  | supported | R
40089 | VA_SF |  |  | 1 | R
40090 | VAr |  |  | supported | R
40091 | VAr_SF |  |  | 1 | R
40092 | PF |  |  | supported | R
40093 | PF_SF |  |  | -3 | R
40094 | WattHours (WH) |  |  | supported | R
40096 | WH_SF |  |  | 1 | R
40097 | DC Amps (DCA) |  |  | unimplemented | R | For this product the DC current is not provided with model 103 but using model 160.
40098 | DCA_SF |  |  | unimplemented | R
40099 | DC Voltage (DCV) |  |  | unimplemented | R | For this product the DC voltage is not provided with model 103 but using model 160.
40100 | DCV_SF |  |  | unimplemented | R
40101 | DC Watts (DCW) |  |  | supported | R
40102 | DCW_SF |  |  | 2 | R
40103 | Cabinet Temperature (TmpCab) |  |  | supported | R
40104 | Heat Sink Temperature (TmpSnk) |  |  | supported | R
40105 | Transformer Temperature (TmpTrns) |  |  | supported | R
40106 | Other Temperature (TmpOt) |  |  | supported | R | For this product the external ambient temperature is provided.
40107 | Tmp_SF |  |  | 0 | R
40108 | Operating State (St) |  |  | supported | R
|  |  | Off (OFF) | supported
|  |  | Sleeping (SLEEPING) | supported
|  |  | Starting (STARTING) | supported
|  |  | MPPT | supported
|  |  | Throttled (THROTTLED) | supported
|  |  | Shutting down (SHUTTING_DOWN) | supported
|  |  | Fault (FAULT) | supported
|  |  | Standby (STANDBY) | unimplemented
40109 | Vendor Operating State (StVnd) |  |  | unimplemented | R
40110 | Event1 (Evt1) |  |  | supported | R
|  |  | Ground fault (GROUND_FAULT) | supported
|  |  | DC over voltage (DC_OVER_VOLT) | supported
|  |  | AC disconnect open (AC_DISCONNECT) | unimplemented
|  |  | DC disconnect open (DC_DISCONNECT) | unimplemented
|  |  | Grid shutdown (GRID_DISCONNECT) | supported
|  |  | Cabinet open (CABINET_OPEN) | unimplemented
|  |  | Manual shutdown (MANUAL_SHUTDOWN) | supported
|  |  | Over temperature (OVER_TEMP) | supported
|  |  | Frequency above limit (OVER_FREQUENCY) | supported
|  |  | Frequency under limit (UNDER_FREQUENCY) | supported
|  |  | AC Voltage above limit (AC_OVER_VOLT) | supported
|  |  | AC Voltage under limit (AC_UNDER_VOLT) | supported
|  |  | Blown String fuse on input (BLOWN_STRING_FUSE) | supported
|  |  | Under temperature (UNDER_TEMP) | supported
|  |  | Generic Memory or Communication error (internal) (MEMORY_LOSS) | supported
|  |  | Hardware test failure (HW_TEST_FAILURE) | supported
40112 | Event Bitfield 2 (Evt2) |  |  | supported | R
40114 | Vendor Event Bitfield 1 (EvtVnd1) |  |  | unimplemented | R
40116 | Vendor Event Bitfield 2 (EvtVnd2) |  |  | unimplemented | R
40118 | Vendor Event Bitfield 3 (EvtVnd3) |  |  | unimplemented | R
40120 | Vendor Event Bitfield 4 (EvtVnd4) |  |  | unimplemented | R

## 120
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40122 | ID |  |  | 120
40123 | L |  |  | 26
40124 | DERTyp |  |  | supported | R
|  |  | PV | supported
|  |  | PV_STOR | supported
40125 | WRtg |  |  | supported | R
40126 | WRtg_SF |  |  | 2 | R
40127 | VARtg |  |  | supported | R
40128 | VARtg_SF |  |  | 2 | R
40129 | VArRtgQ1 |  |  | supported | R
40130 | VArRtgQ2 |  |  | supported | R
40131 | VArRtgQ3 |  |  | supported | R
40132 | VArRtgQ4 |  |  | supported | R
40133 | VArRtg_SF |  |  | 2 | R
40134 | ARtg |  |  | supported | R
40135 | ARtg_SF |  |  | 0 | R
40136 | PFRtgQ1 |  |  | supported | R
40137 | PFRtgQ2 |  |  | supported | R
40138 | PFRtgQ3 |  |  | supported | R
40139 | PFRtgQ4 |  |  | supported | R
40140 | PFRtg_SF |  |  | -1 | R
40141 | WHRtg |  |  | unimplemented | R
40142 | WHRtg_SF |  |  | unimplemented | R
40143 | AhrRtg |  |  | unimplemented | R
40144 | AhrRtg_SF |  |  | unimplemented | R
40145 | MaxChaRte |  |  | unimplemented | R
40146 | MaxChaRte_SF |  |  | unimplemented | R
40147 | MaxDisChaRte |  |  | unimplemented | R
40148 | MaxDisChaRte_SF |  |  | unimplemented | R
40149 | Pad |  |  |  | R

## 121
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40150 | ID |  |  | 121
40151 | L |  |  | 30
40152 | WMax |  |  | supported | RW
40153 | VRef |  |  | supported | RW
40154 | VRefOfs |  |  | supported | RW
40155 | VMax |  |  | unimplemented | RW
40156 | VMin |  |  | unimplemented | RW
40157 | VAMax |  |  | supported | RW
40158 | VArMaxQ1 |  |  | unimplemented | RW
40159 | VArMaxQ2 |  |  | unimplemented | RW
40160 | VArMaxQ3 |  |  | unimplemented | RW
40161 | VArMaxQ4 |  |  | unimplemented | RW
40162 | WGra |  |  | unimplemented | RW
40163 | PFMinQ1 |  |  | unimplemented | RW
40164 | PFMinQ2 |  |  | unimplemented | RW
40165 | PFMinQ3 |  |  | unimplemented | RW
40166 | PFMinQ4 |  |  | unimplemented | RW
40167 | VArAct |  |  | unimplemented | RW
|  |  | SWITCH | unimplemented
|  |  | MAINTAIN | unimplemented
40168 | ClcTotVA |  |  | unimplemented | RW
|  |  | VECTOR | unimplemented
|  |  | ARITHMETIC | unimplemented
40169 | MaxRmpRte |  |  | unimplemented | RW
40170 | ECPNomHz |  |  | unimplemented | RW
40171 | ConnPh |  |  | unimplemented | RW
|  |  | A | unimplemented
|  |  | B | unimplemented
|  |  | C | unimplemented
40172 | WMax_SF |  |  | 0 | R
40173 | VRef_SF |  |  | 0 | R
40174 | VRefOfs_SF |  |  | 0 | R
40175 | VMinMax_SF |  |  | unimplemented | R
40176 | VAMax_SF |  |  | 0 | R
40177 | VArMax_SF |  |  | unimplemented | R
40178 | WGra_SF |  |  | unimplemented | R
40179 | PFMin_SF |  |  | unimplemented | R
40180 | MaxRmpRte_SF |  |  | unimplemented | R
40181 | ECPNomHz_SF |  |  | unimplemented | R

## 123
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40182 | ID |  |  | 123
40183 | L |  |  | 24
40184 | Conn_WinTms |  |  | supported | RW
40185 | Conn_RvrtTms |  |  | supported | RW | When reversion time (RvrtTms) value is set to 0 the associated control settings will be applied permanently as new "default" values. This leads to the following considerations: - In this case the control settings will be saved on non-volatile storage and so the user application should not send frequent commands using RvrtTms = 0 because this can damage the memory support; - When new settings are sent using RvrtTms > 0 then they will be applied until the given timeout is expired. After the timeout the settings will be restored to the "default" ones configured with the last command sent with RvrtTms = 0;
40186 | Conn |  |  | supported | RW
|  |  | DISCONNECT | supported
|  |  | CONNECT | supported
40187 | WMaxLimPct |  |  | supported | RW
40188 | WMaxLimPct_WinTms |  |  | supported | RW
40189 | WMaxLimPct_RvrtTms |  |  | supported | RW | When reversion time (RvrtTms) value is set to 0 the associated control settings will be applied permanently as new "default" values. This leads to the following considerations: - In this case the control settings will be saved on non-volatile storage and so the user application should not send frequent commands using RvrtTms = 0 because this can damage the memory support; - When new settings are sent using RvrtTms > 0 then they will be applied until the given timeout is expired. After the timeout the settings will be restored to the "default" ones configured with the last command sent with RvrtTms = 0;
40190 | WMaxLimPct_RmpTms |  |  | supported | RW
40191 | WMaxLim_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40192 | OutPFSet |  |  | supported | RW
40193 | OutPFSet_WinTms |  |  | supported | RW
40194 | OutPFSet_RvrtTms |  |  | supported | RW | When reversion time (RvrtTms) value is set to 0 the associated control settings will be applied permanently as new "default" values. This leads to the following considerations: - In this case the control settings will be saved on non-volatile storage and so the user application should not send frequent commands using RvrtTms = 0 because this can damage the memory support; - When new settings are sent using RvrtTms > 0 then they will be applied until the given timeout is expired. After the timeout the settings will be restored to the "default" ones configured with the last command sent with RvrtTms = 0;
40195 | OutPFSet_RmpTms |  |  | supported | RW
40196 | OutPFSet_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40197 | VArWMaxPct |  |  | unimplemented | RW
40198 | VArMaxPct |  |  | unimplemented | RW
40199 | VArAvalPct |  |  | supported | RW
40200 | VArPct_WinTms |  |  | supported | RW
40201 | VArPct_RvrtTms |  |  | supported | RW | When reversion time (RvrtTms) value is set to 0 the associated control settings will be applied permanently as new "default" values. This leads to the following considerations: - In this case the control settings will be saved on non-volatile storage and so the user application should not send frequent commands using RvrtTms = 0 because this can damage the memory support; - When new settings are sent using RvrtTms > 0 then they will be applied until the given timeout is expired. After the timeout the settings will be restored to the "default" ones configured with the last command sent with RvrtTms = 0;
40202 | VArPct_RmpTms |  |  | supported | RW
40203 | VArPct_Mod |  |  | unimplemented | RW
|  |  | NONE | unimplemented
|  |  | WMax | unimplemented
|  |  | VArMax | unimplemented
|  |  | VArAval | unimplemented
40204 | VArPct_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40205 | WMaxLimPct_SF |  |  | 0 | R
40206 | OutPFSet_SF |  |  | -4 | R
40207 | VArPct_SF |  |  | -1 | R

## 160
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40208 | ID |  |  | 160
40209 | L |  |  | 28
40210 | Current Scale Factor (DCA_SF) |  |  | -1 | R
40211 | Voltage Scale Factor (DCV_SF) |  |  | -1 | R
40212 | Power Scale Factor (DCW_SF) |  |  | 2 | R
40213 | Energy Scale Factor (DCWH_SF) |  |  | unimplemented | R
40214 | Global Events (Evt) |  |  | unimplemented | R
|  |  | Ground Fault (GROUND_FAULT) | unimplemented
|  |  | Input Over Voltage (INPUT_OVER_VOLTAGE) | unimplemented
|  |  | Reserved (RESERVED) | unimplemented
|  |  | DC Disconnect (DC_DISCONNECT) | unimplemented
|  |  | Cabinet Open (CABINET_OPEN) | unimplemented
|  |  | Manual Shutdown (MANUAL_SHUTDOWN) | unimplemented
|  |  | Over Temperature (OVER_TEMP) | unimplemented
|  |  | Blown Fuse (BLOWN_FUSE) | unimplemented
|  |  | Under Temperature (UNDER_TEMP) | unimplemented
|  |  | Memory Loss (MEMORY_LOSS) | unimplemented
|  |  | Arc Detection (ARC_DETECTION) | unimplemented
|  |  | Test Failed (TEST_FAILED) | unimplemented
|  |  | Under Voltage (INPUT_UNDER_VOLTAGE) | unimplemented
|  |  | Over Current (INPUT_OVER_CURRENT) | unimplemented
40216 | Number of Modules (N) |  |  | supported | R
40217 | Timestamp Period (TmsPer) |  |  | unimplemented | R
40218 | Input ID (ID) | 1 |  | supported | R
40219 | Input ID Sting (IDStr) | 1 |  | supported | R
40227 | DC Current (DCA) | 1 |  | supported | R
40228 | DC Voltage (DCV) | 1 |  | supported | R
40229 | DC Power (DCW) | 1 |  | supported | R
40230 | Lifetime Energy (DCWH) | 1 |  | unimplemented | R
40232 | Timestamp (Tms) | 1 |  | unimplemented | R
40234 | Temperature (Tmp) | 1 |  | unimplemented | R
40235 | Operating State (DCSt) | 1 |  | unimplemented | R
|  |  | Off (OFF) | unimplemented
|  |  | Sleeping (SLEEPING) | unimplemented
|  |  | Starting (STARTING) | unimplemented
|  |  | MPPT | unimplemented
|  |  | Throttled (THROTTLED) | unimplemented
|  |  | Shutting Down (SHUTTING_DOWN) | unimplemented
|  |  | Fault (FAULT) | unimplemented
|  |  | Standby (STANDBY) | unimplemented
|  |  | Test (TEST) | unimplemented
|  |  | Reserved (RESERVED) | unimplemented
40236 | Module Events (DCEvt) | 1 |  | unimplemented | R
|  |  | Ground Fault (GROUND_FAULT) | unimplemented
|  |  | Input Over Voltage (INPUT_OVER_VOLTAGE) | unimplemented
|  |  | Reserved (RESERVED) | unimplemented
|  |  | DC Disconnect (DC_DISCONNECT) | unimplemented
|  |  | Cabinet Open (CABINET_OPEN) | unimplemented
|  |  | Manual Shutdown (MANUAL_SHUTDOWN) | unimplemented
|  |  | Over Temperature (OVER_TEMP) | unimplemented
|  |  | Blown Fuse (BLOWN_FUSE) | unimplemented
|  |  | Under Temperature (UNDER_TEMP) | unimplemented
|  |  | Memory Loss (MEMORY_LOSS) | unimplemented
|  |  | Arc Detection (ARC_DETECTION) | unimplemented
|  |  | Test Failed (TEST_FAILED) | unimplemented
|  |  | Under Voltage (INPUT_UNDER_VOLTAGE) | unimplemented
|  |  | Over Current (INPUT_OVER_CURRENT) | unimplemented

## 403
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40238 | ID |  |  | 403
40239 | L |  |  | 48
40240 | DCA_SF |  |  | 0 | R
40241 | DCAhr_SF |  |  | unimplemented | R
40242 | DCV_SF |  |  | 0 | R
40243 | Rating (DCAMax) |  |  | supported | R
40244 | N |  |  | supported | R
40245 | Event (Evt) |  |  | supported | R
|  |  | LOW_VOLTAGE | unimplemented
|  |  | LOW_POWER | unimplemented
|  |  | LOW_EFFICIENCY | unimplemented
|  |  | CURRENT | unimplemented
|  |  | VOLTAGE | unimplemented
|  |  | POWER | unimplemented
|  |  | PR | unimplemented
|  |  | DISCONNECTED | unimplemented
|  |  | FUSE_FAULT | supported
|  |  | COMBINER_FUSE_FAULT | unimplemented
|  |  | COMBINER_CABINET_OPEN | unimplemented
|  |  | TEMP | unimplemented
|  |  | GROUNDFAULT | unimplemented
|  |  | REVERSED_POLARITY | unimplemented
|  |  | INCOMPATIBLE | unimplemented
|  |  | COMM_ERROR | unimplemented
|  |  | INTERNAL_ERROR | unimplemented
|  |  | THEFT | unimplemented
|  |  | ARC_DETECTED | unimplemented
40247 | Vendor Event (EvtVnd) |  |  | unimplemented | R
40249 | Amps (DCA) |  |  | supported | R
40250 | Amp-hours (DCAhr) |  |  | unimplemented | R
40252 | Voltage (DCV) |  |  | supported | R
40253 | Temp (Tmp) |  |  | unimplemented | R
40254 | InDCA_SF |  |  | 0 | R
40255 | InDCAhr_SF |  |  | unimplemented | R
40256 | ID (InID) | 1 |  | supported | R
40257 | Event (InEvt) | 1 |  | supported | R
|  |  | LOW_VOLTAGE | unimplemented
|  |  | LOW_POWER | unimplemented
|  |  | LOW_EFFICIENCY | unimplemented
|  |  | CURRENT | unimplemented
|  |  | VOLTAGE | unimplemented
|  |  | POWER | unimplemented
|  |  | PR | unimplemented
|  |  | DISCONNECTED | unimplemented
|  |  | FUSE_FAULT | supported
|  |  | COMBINER_FUSE_FAULT | unimplemented
|  |  | COMBINER_CABINET_OPEN | unimplemented
|  |  | TEMP | unimplemented
|  |  | GROUNDFAULT | unimplemented
|  |  | REVERSED_POLARITY | unimplemented
|  |  | INCOMPATIBLE | unimplemented
|  |  | COMM_ERROR | unimplemented
|  |  | INTERNAL_ERROR | unimplemented
|  |  | THEFT | unimplemented
|  |  | ARC_DETECTED | unimplemented
40259 | Vendor Event (InEvtVnd) | 1 |  | unimplemented | R
40261 | Amps (InDCA) | 1 |  | supported | R
40262 | Amp-hours (InDCAhr) | 1 |  | unimplemented | R
40264 | ID (InID) | 2 |  | supported | R
40265 | Event (InEvt) | 2 |  | supported | R
40267 | Vendor Event (InEvtVnd) | 2 |  | unimplemented | R
40269 | Amps (InDCA) | 2 |  | supported | R
40270 | Amp-hours (InDCAhr) | 2 |  | unimplemented | R
40272 | ID (InID) | 3 |  | supported | R
40273 | Event (InEvt) | 3 |  | supported | R
40275 | Vendor Event (InEvtVnd) | 3 |  | unimplemented | R
40277 | Amps (InDCA) | 3 |  | supported | R
40278 | Amp-hours (InDCAhr) | 3 |  | unimplemented | R
40280 | ID (InID) | 4 |  | supported | R
40281 | Event (InEvt) | 4 |  | supported | R
40283 | Vendor Event (InEvtVnd) | 4 |  | unimplemented | R
40285 | Amps (InDCA) | 4 |  | supported | R
40286 | Amp-hours (InDCAhr) | 4 |  | unimplemented | R